## Item code and BOQ
Sl No | Item Code | Item Name | UoM | Qty/Site | Qty | Total Qty
A |  | Tower
1 | FA00816 | 35M 3Legged Tower foundation (anchor bolts, templates, etc) | Set | 1 | 2 | 2
2 | FA00817 | 30M 3Legged Tower foundation (anchor bolts, templates, etc) | Set | 1 | 34 | 34
3 | FA00818 | 25M 3Legged Tower foundation (anchor bolts, templates, etc) | Set | 1 | 28 | 28
4 | FA00819 | 20M 3Legged Tower foundation (anchor bolts, templates, etc) | Set | 1 | 6 | 6
5 | FA00820 | 15M 4Legged Tower foundation (anchor bolts, templates, etc) with earthing | Set | 1 | 1 | 1
6 | FA00601 | Tower: 35M self-supporting Complete supply, fabrication, galvanization (min 85micron) self-supporting 3-legged angular construction with separate Earthing provisions. Tower should have name plate (supplier company name, Height and year of installation).Antenna mounting structures (3m) and aviation lamp with cable and accesories as per the Specifications | Nos | 1 | 2 | 2
7 | FA00296 | Tower: 30M self-supporting Complete supply, fabrication, galvanization (min 85micron) self-supporting 3-legged angular construction with separate Earthing provisions. Tower should have name plate (supplier company name, Height and year of installation).Antenna mounting structures (3m) and aviation lamp with cable and accesories as per the Specification | Nos | 1 | 34 | 34
8 | FA00297 | Tower 25M self-supporting Complete supply, fabrication, galvanization (min 85micron) self-supporting 3-legged angular construction with separate Earthing provisions. Tower should have name plate (supplier company name, Height and year of installation).Antenna mounting structures (3m) and aviation lamps as per the Specification25 | Nos | 1 | 28 | 28
9 | FA00298 | Tower: 20M self-supporting Complete supply, fabrication, galvanization (min 85micron) self-supporting 3-legged angular construction with separate Earthing provisions. Tower should have name plate (supplier company name, Height and year of installation).Antenna mounting structures (3m) and aviation lamps as per the Specification 6 | Nos | 1 | 6 | 6
B |  | Monopoles
1 | FA00821 | 15M Monopole foundation (anchor bolts, templates, etc) | Set | 1 | 44 | 44
2 | FA00303 | Monopole: 15M With separate Earthing provisions. Tower should have name plate (company name (Bhutan Telecom Limited, Height and year of installation), 3 LED Lamp with LDR Sensor, 3 nos of antenna mounting structure (1.5m), 4 nos of radio mounting structure (500-600mm) with Meter Boix, Fall Arrestor with Wire rope of 8mm & Rope Grab (Both Material should be Stainless Steel 316) arrangement as shown in the drawing. | Set | 1 | 38 | 38
3 | FA00304 | Monopole: 15M With separate Earthing provisions. Tower should have name plate (company name (Bhutan Telecom Limited, Height and year of installation), 2 LED Lamp with LDR Sensor, 3 nos of antenna mounting structure (1.5m), 4 nos of radio mounting structure (500-600mm). with Meter Boix, Fall Arrestor with Wire rope of 8mm & Rope Grab (Both Material should be Stainless Steel 316) arrangement as shown in the drawing. | Set | 1 | 3 | 3
4 | FA00826 | 15M Flange Joint With separate Earthing provisions (as per design attached in RFP) Tower should have name plate [company name (Bhutan Telecom Limited, Height and year of installation), 3 LED Lamp with LDR Sensor and lighting cables and accessories] | Set | 1 | 3 | 3
C |  | Shelter
1 | FA00822 | Supply of Pre-fabricated shelter with external sheet roofing and lighting facility: Ext:3600x2600x2500(LxWxH in mm) foundation materials. | Set | 1 | 70 | 70
2 | FA00823 | Supply of Pre-fabricated shelter with external sheet roofing and lighting facility: Ext:6000x3600x2600(LxWxH in mm) foundation materials | Set | 1 | 1 | 1
3 | FA00300 | Pre-fabricated shelter with external sheet roofing and lighting facility: Ext:3600x2600x2500(LxWxH in mm). Panel with Foam-60mm, Material of skin- 0.6mmx0.6mm pre- Floor- Ply 18mm and PVC 2mm | Set | 1 | 70 | 70
4 | FA00824 | Supply of Pre-fabricated shelter with external sheet roofing and lighting facility: Ext:6000x3600x2600(LxWxH in mm). Panel with Foam-60mm, Material of skin- 0.6mmx0.6mm pre- Floor- Ply 18mm and PVC 2mm (as per drawing attached in RFP) | Set | 1 | 1 | 1
D |  | Powe Equipment (AC )
1 | FA00260 | VRLA Battery- 2V/450 AH @ C10 @ 1.75 ECV @ 27 Deg.C (+)48V DC, 450 AH * 2 nos = 900 AH per site with battery racks, stands, connectors, battery remover, transparent covers,etc. Make:HBL/Amaraja/Rocket/NED | Banks | 1 | 47 | 47
2 | FA00825 | VRLA Battery- 2V/760 AH @ C10 @ 1.75 ECV @ 27 Deg.C (+)48V DC, 760 AH * 2 nos = 1520 AH per site with battery racks, stands, connectors, battery remover, transparent covers,etc Make:HBL/Amaraja/Rocket/NED | Banks | 1 | 1 | 1
3 | FA00602 | SMPS Rectifier Battery Charger, IP Vac = 180 – 280 Vac; OP = (-48V DC), 500 Amps, Modular Type with minimum 8 No of Modules and 8 slots of 60 Amps per module. Must have load facility to connect both critical and non critical loads using appropriate MCBs and HRC Fuse. Also should have an inbuilt controller having the following features to monitor the status of the rectifier, battery, room temperature, ac mains available or not, DG supply available or not, rectifier failure alarm, load on battery, load on AC or DG. All these parameters are to be monitored remotely using LAN/Modem, GSM, GPRS, Web browser. Remote alarming using dry contacts/SNMP. ( Vertiv/Delta / benning/Dynamic Power/Exicom) | Set | 1 | 50 | 50
4 | FA00275 | DCPDB ( Rating: 100amps, -48VDCPDC. This Pre-wired Power Distribution Board shall provide all the connections to battery bank with proper rating of DC MCBs and additional battery charging facilities. MCB dual pole rating as 63A 2 nos, 32A 4nos, 16A 10nos | nos | 1 | 50 | 50
5 | FA00276 | ACPDB (Rating: 100 amps, 230 V AC Pre-wired/assembled with inbuilt MCBs (2P, 32 amps - 4 Nos, 2 P, 16 amps- 8 Nos, 2P, 10 amps- 6 nos ) | nos | 1 | 50 | 50
6 | FA00441 | DC Power Cable 70 Sq.mm ( RED) 1.1KV, IC PVC Insulated, unarmoured multi-strand copper Cable ( 40M per site) (Make: Polycab/ RR/Havell's) | nos | 1 | 50 | 50
7 | FA00442 | DC Power Cable 70 Sqmm ( Blue/Black) 1.1KV, IC PVC Insulated, unarmoured multi-strand copper Cable ( 40M per site) (Make: Polycab/ RR/Havell's) | nos | 1 | 50 | 50
8 | FA00279 | Rectifier Cable (RED) , 20 Sqmm, 25 Meters per site (Make: Polycab/ RR/Havell's) | nos | 1 | 50 | 50
9 | FA00280 | Rectifier Cable (Blue/Black), 20 Sq.mm, 25 Meters per site (Make: Polycab/ RR/Havell's) | nos | 1 | 50 | 50
10 | FA00603 | AC Power Cables for Aircon ( 1.1 kV, 3 C PVC Insulated, unarmored multi-strand copper cable), 4 sq.mm, 25m per site (Make: Polycab/ RR/Havell's) | nos | 1 | 50 | 50
11 | FA00604 | Electrical Earthing Cable , 4 Sq.mm (Green Colour) 100 Mtrs per site (Make: Polycab/ RR/Havell's) | nos | 1 | 50 | 50
12 | FA00284 | Chemical Based Earthing System with -48VDC DC SPD:CHEMICAL EARTHING . CPRI /ISO Approved Chemical earthing . Tri-rod pre welded copper (5 ft long 12mm Dia. # 2 set), GAF (Chemical) # 2X40 kg, Copper revit # 10 nos, Earth Distribution bus bar # 2 Nos, earth pit cover, copper strip 25X3 mm. # 30 mtr per set, salt # 2 X 10 kg per set, Charcoal # 2 x 5 kg per set, connectors, lugs,clamps, etc Surge Protection Device, Un (dc) = 48V, Uc (dc) = 75V, In (8/20μs)= 40kA with appropriate MCB and BOX prewired with fault indicator available (BSMC/Eritech/ Icon/Pragati) | Set | 1 | 50 | 50
13 | FA00605 | Free Cooling Unit, Air outlet configuration Gravity based dampers without any fan. Worm-protection net. The assembly shall ensure no water / rain leak into the shelter. The damper is closed when AC is operating and damper will open when FCU is operating Air inlet configuration Rain-proof cover, 48 V DC powered Axial flow fan, air filtering net, Gravity based dampers, worm-protection net, fine filters Filtration 90% down to 20 microns Airflow at full capacity 1200 + 200 CFM at 48 V (May be suitably designed as per site requirement). 2/4 fans may be used to meet the total CFM requirement, if required. Microprocessor based controller The Control unit (controller) shall be provided to automatically control the operation of FCU in all possible conditions in telecommunications equipment room in auto mode. It shall also have facility to switch on and off the air conditioning units installed in the room. Auto Mode Operation – 1. Under favorable environment conditions, the controller shall switch off the air-conditioning unit and start free cooling. 2. Whenever room temperature rises above set temperature, then controller shall switch off the FCU / associated dampers and switch on the air-conditioning unit. 3. The controller shall switch off the FCU / associated dampers if battery voltage drop below set voltage. 4. Controller shall measure Run Hour of FCU Mode and Cooling Mode. 5. When ever the temperature of BTS exceeds 40 Deg C on a/c of AC failure or any other reason, there should be a provision to start Free Cooling Unit again through controller for emergency cooling ( Pragati/ICON/Delta/Vertiv) | Set | 1 | 50 | 50
14 | FA00606 | Split Type Airconditioners ( Stabiliser free, inverter air conditioner: 1.5T, Single Phase,50Hz,Input Volt=150 - 230V, Split type with appropriate rating of MCBs,High Low Pressure Pipe=4 m each, outlet drain pipe =10 m each flexible, cable size=4 sqmm cu stranded 3 core=5 m, MCBs=SPN, 16Amps, with stand to fix the outdoor unit. Refrigerant: R32 (Make: Samsung/Hitachi/Toshiba/Blue star/ LG/Voltas/Godrej/Daikin) | Set | 1 | 50 | 50
15 | FA00475 | Earth Cable ( Green or Green/yellow mixed), PVC insulated single multi strand core copper conductor ( 1.1KV) 1C , 25 sq.mm (50M per site) (Make: Polycab/ RR/Havell's) | nos | 1 | 50 | 50
16 | FA00287 | LPS ( Lightening Protection System) - 1. Lightning Arrester: Supply of Lightning Protection System that works on Early Streamer Emission Technology having coverage radius >80 mtrs when mounted at a height of 05 mtrs giving level I protection. Tested international high-tension laboratory, tested/approved by CPRI, India 2. FRP Mast-5 mtrs. 3.Lightning Strike Counter with IP-65 Enclosure 4. HVSC Down Copper conductor 5. Chemical Earthing: i. Tri-rod 100% copper (5 ft long 17mm Dia # 2 set) welded together and with connection strip & fitted with 4 sets for connecting ii. GEM (Chemical) # 2X40 kg iii. Copper rivet # 10 nos iv. Earth Distribution bus bar # 2 Nos, v. Earth pit cover - 2 nos. vi. Copper (100% copper) strip 25X3 mm- 30 mtr vii. Connectors, lugs, clamps, etc (Make: LPI/Erico/Bakiral) | Set | 1 | 50 | 50
17 | FA00288 | TVSS/SPD: Surge Protection Device, Single Phase (230V AC), Max discharge current 100kA (10/350 µs), Fault Indicator Available, Protection Mode: L-N/N-PE, with appropriate MCB and Box, prewired (Make: LPI/Emerson/Erico/Eaton/Phoenix) | Set | 1 | 50 | 50
18 | FA00607 | Copper Terminal Ends (Ring Type)/Lugs, 4 sq.mm (20 nos Ring Type ) | Pkt | 1 | 50 | 50
19 | FA00608 | Copper Terminal Ends (Ring Type)/Lugs, 4 sq.mm ( 10 nos pin type) | Pkt | 1 | 50 | 50
20 | FA00609 | Copper Terminal Lugs, 25 sq.mm ( 20 nos Ring type) | Pkt | 1 | 50 | 50
21 | FA00610 | Copper Terminal Ends (Ring Type)/Lugs, 25 sq.mm ( 5 nos pin type) | Pkt | 1 | 50 | 50
22 | FA00611 | Copper Terminal Ends Lugs, 70 sq.mm ( 15 nos Ring type) | Pkt | 1 | 50 | 50
23 | FA00488 | PVC Insulation Tape RED | Roll | 2 | 100 | 200
24 | FA00489 | PVC Insulation Tape ( Black) | Roll | 2 | 100 | 200
25 | FA00492 | PVC Insulation Tape ( Green) | Roll | 2 | 100 | 200
26 | FA00291 | Cable Tie , Natural 6", Inner Unit Pack: 100 pieces per box | Box | 1 | 50 | 50
27 | FA00292 | Cable Tie, Natural 8", Inner Unit Pack: 100 pieces per box | Box | 1 | 50 | 50
28 | FA00293 | Cable Tie, Natural 12", inner Unit Pack: 100 pieces per box | Box | 1 | 50 | 50
29 | FA00294 | Cable Tie, Heavy Duty Weather Resistant 8", Inner Unit Pack: 100 per box | Box | 1 | 50 | 50
30 | FA00295 | Cable Tie , Heavy Duty Weather Resistant 12", Inner Unit Pack: 100 pieces per box | Box | 1 | 50 | 50
E |  | Solar Power Equipment ( Solar 10KW)
1 | FA00260 | VRLA Battery- 2V/450 AH @ C10 @ 1.75 ECV @ 27 Deg.C (+)48V DC, 450 AH * 2 nos = 900 AH per site with battery racks, stands, connectors, battery remover, transparent covers,etc. Make:HBL/Amaraja/Rocket/NED | Banks | 1 | 11 | 11
2 | FA00613 | Solar Modules/Panels with structures ie 1.5M above the ground level, Wattage (Wp): 335 Wp Voltage (Vmp) : 36 V Current (Imp) : 8 Amps with mounting structures (6 module structure), pre-assembled connectors ( 10KW capacity) ( Tata BP/ Vikram solar/ Mosebaer) 30 Module per site (Tata BP/ Vikram solar/ Mosebaer/Waree/Equivalent) | PV/module | 30 | 330 | 9900
3 | FA00827 | Solar Structure ie 1.5M above ground level foundation bolts and templates for 6 module structure with 30 panels. | Set | 1 | 11 | 11
4 | FA00642 | Surge Protection Device, Un (dc) = 48V, Uc (dc) = 75V, In (8/20μs)= 40kA with appropriate MCB and BOX prewired with fault indicator available, Make Erico/Eritech/Tercel/Dehn/LPI/Phoenix | nos | 1 | 11 | 11
5 | FA00276 | ACPDB (Rating: 100 amps, 230 V AC Pre-wired/assembled with inbuilt MCBs (2P, 32 amps - 4 Nos, 2 P, 16 amps- 8 Nos, 2P, 10 amps- 6 nos ) | nos | 1 | 11 | 11
6 | FA00275 | DCPDB ( Rating: 100amps, -48VDCPDC. This Pre-wired Power Distribution Board shall provide all the connections to battery bank with proper rating of DC MCBs and additional battery charging facilities. MCB dual pole rating as 63A 2 nos, 32A 4nos, 16A 10nos | nos | 1 | 11 | 11
7 | FA00643 | Solar-DG-Utility-Battery Hybrid MPPT system, modular type, 2 kW, 500 Amps, having min 5 (Five) solar mppt modules of 40 Amps capacity and 3 additional MPPT slots . 6 nos of rectifier module of capacity 80 amps and 2 additional rectifier slots having the following features: Must have load facility to connect both critical and non critical loads using appropriate MCBs and HRC Fuse. Further, the system also should have min two nos of appropriate rating of HRC fuses for connecting of min two battery banks of min 450 Ah per bank. Also should have an inbuilt controller having the following features to monitor the status of the rectifier, battery, room temperature, ac mains available or not, DG supply available or not, rectifier failure alarm, load on battery, load on AC or DG. All these parameters are to be monitored remotely using LAN/Modem, GSM, GPRS, Web browser. Remote alarming using dry contacts/SNMP: 1. Solar Converter Specs: Input voltage (DC), Vertiv/Delta/Eltek/Dynamic Power/Exicom | Set | 1 | 11 | 11
8 | FA00614 | Solar DC Power Cables: Specification: 1. Construction: tinned copper conductor IEC 60228, insulation/sheath: electron beam cross linked halogen free & flame retardant component. 2. Electrical: Max permissible operating voltage: DC 1.8kV 3. Temperature: -40 to +90 Deg C., Solar Panel to AJB: 6 sq.mm, (RED) 50 m per site (Polycab/ RR/Havell's/Relison ) | nos | 1 | 11 | 11
9 | FA00615 | Solar DC Power Cables: Specification: 1. Construction: tinned copper conductor IEC 60228, insulation/sheath: electron beam cross linked halogen free & flame retardant component. 2. Electrical: Max permissible operating voltage: DC 1.8kV 3. Temperature: -40 to +90 Deg C., ) Solar Panel to AJB: 6 sq.mm, (BLACK) 50 m per site (Polycab/ RR/Havell's /Relison | nos | 1 | 11 | 11
10 | FA00617 | Solar Cable Armoured Specification for 10KW Solar system: 1. Construction: tinned copper conductor IEC 60228, insulation/sheath: electron beam cross linked halogen free & flame retardant component. 2. Electrical: Max permissible operating voltage: DC 1.8kV 3. Temperature: -40 to +90 Deg C. 4. Armour: braid of galvanized steel, , AJB to Hybrid Rectifier: 16sq.mm, 2C, solar dc cable, multistand copper conductor 100M per site (Polycab/ RR/Havell's/Relison ) | nos | 1 | 11 | 11
11 | FA00620 | DC Power Cable, Hybrid Charger to Battery Bank: 70 sq.mm, 1C, PVC insulated, multistrand copper conductor (RED ) 50 m per site (Polycab/ RR/Havell's /Relison) | nos | 1 | 11 | 11
12 | FA00621 | DC Power Cable, Hybrid Charger to Battery Bank: 70 sq.mm, 1C, PVC insulated, multistrand copper conductor (BLACK ) 50 m per site (Polycab/ RR/Havell's /Relison) | nos | 1 | 11 | 11
13 | FA00017 | Installation Materials | lot | 1 | 11 | 11
14 | FA00284 | Chemical Based Earthing System with -48VDC DC SPD:CHEMICAL EARTHING . CPRI /ISO Approved Chemical earthing . Tri-rod pre welded copper (5 ft long 12mm Dia. # 2 set), GAF (Chemical) # 2X40 kg, Copper revit # 10 nos, Earth Distribution bus bar # 2 Nos, earth pit cover, copper strip 25X3 mm. # 30 mtr per set, salt # 2 X 10 kg per set, Charcoal # 2 x 5 kg per set, connectors, lugs,clamps, etc Surge Protection Device, Un (dc) = 48V, Uc (dc) = 75V, In (8/20μs)= 40kA with appropriate MCB and BOX prewired with fault indicator available (BSMC/Eritech/ Icon/Pragati) | Set | 1 | 11 | 11
15 | FA00475 | Earth Cable ( Green or Green/yellow mixed), PVC insulated single multi strand core copper conductor ( 1.1KV) 1C , 25 sq.mm (50M per site) (Make: Polycab/ RR/Havell's) | nos | 1 | 11 | 11
16 | FA00605 | Free Cooling Unit, Air outlet configuration Gravity based dampers without any fan. Worm-protection net. The assembly shall ensure no water / rain leak into the shelter. The damper is closed when AC is operating and damper will open when FCU is operating Air inlet configuration Rain-proof cover, 48 V DC powered Axial flow fan, air filtering net, Gravity based dampers, worm-protection net, fine filters Filtration 90% down to 20 microns Airflow at full capacity 1200 + 200 CFM at 48 V (May be suitably designed as per site requirement). 2/4 fans may be used to meet the total CFM requirement, if required. Microprocessor based controller The Control unit (controller) shall be provided to automatically control the operation of FCU in all possible conditions in telecommunications equipment room in auto mode. It shall also have facility to switch on and off the air conditioning units installed in the room. Auto Mode Operation – 1. Under favorable environment conditions, the controller shall switch off the air-conditioning unit and start free cooling. 2. Whenever room temperature rises above set temperature, then controller shall switch off the FCU / associated dampers and switch on the air-conditioning unit. 3. The controller shall switch off the FCU / associated dampers if battery voltage drop below set voltage. 4. Controller shall measure Run Hour of FCU Mode and Cooling Mode. 5. When ever the temperature of BTS exceeds 40 Deg C on a/c of AC failure or any other reason, there should be a provision to start Free Cooling Unit again through controller for emergency cooling ( Pragati/ICON/Delta/Vertiv) | Set | 1 | 11 | 11
17 | FA00622 | DC/AC lighting system in Shelter, 48V dc light or 230v AC tubelight with switch | Set | 1 | 11 | 11
18 | FA00649 | AC lighting system in Shelter, 230v AC tubelight with switch & accessories | Set | 1 | 11 | 11
19 | FA00287 | LPS ( Lightening Protection System) - 1. Lightning Arrester: Supply of Lightning Protection System that works on Early Streamer Emission Technology having coverage radius >80 mtrs when mounted at a height of 05 mtrs giving level I protection. Tested international high-tension laboratory, tested/approved by CPRI, India 2. FRP Mast-5 mtrs. 3.Lightning Strike Counter with IP-65 Enclosure 4. HVSC Down Copper conductor 5. Chemical Earthing: i. Tri-rod 100% copper (5 ft long 17mm Dia # 2 set) welded together and with connection strip & fitted with 4 sets for connecting ii. GEM (Chemical) # 2X40 kg iii. Copper rivet # 10 nos iv. Earth Distribution bus bar # 2 Nos, v. Earth pit cover - 2 nos. vi. Copper (100% copper) strip 25X3 mm- 30 mtr vii. Connectors, lugs, clamps, etc (Make: LPI/Erico/Bakiral) | Set | 1 | 11 | 11
20 | FA00606 | Split Type Airconditioners ( Stabiliser free, inverter air conditioner: 1.5T, Single Phase,50Hz,Input Volt=150 - 230V, Split type with appropriate rating of MCBs,High Low Pressure Pipe=4 m each, outlet drain pipe =10 m each flexible, cable size=4 sqmm cu stranded 3 core=5 m, MCBs=SPN, 16Amps, with stand to fix the outdoor unit. Refrigerant: R32 (Make: Samsung/Hitachi/Toshiba/Blue star/ LG/Voltas/Godrej/Daikin) | Set | 1 | 11 | 11
21 | FA00645 | Solar Junction Box , Array Junction Box (min 4 inputs and 1 output), | Set | 5 | 55 | 275
22 | FA00625 | Copper Terminal Lugs, 6 sq.mm ( 20 nos Ring type) | Pkt | 1 | 11 | 11
23 | FA00626 | Copper Terminal Lugs, 6 sq.mm ( 10 nos pin type) | Pkt | 1 | 11 | 11
24 | FA00609 | Copper Terminal Lugs, 25 sq.mm ( 20 nos Ring type) | Pkt | 1 | 11 | 11
25 | FA00840 | Copper Terminal Lugs, 25 sq.mm ( 10 nos pin type) | Pkt | 1 | 11 | 11
26 | FA00611 | Copper Terminal Ends Lugs, 70 sq.mm ( 15 nos Ring type) | Pkt | 1 | 11 | 11
27 | FA00651 | Copper Terminal Lugs, 16 sq.mm (25 nos pin Type ) | Pkt | 1 | 11 | 11
28 | FA00488 | PVC Insulation Tape RED | Roll | 2 | 22 | 44
29 | FA00489 | PVC Insulation Tape ( Black) | Roll | 2 | 22 | 44
30 | FA00492 | PVC Insulation Tape ( Green) | Roll | 2 | 22 | 44
31 | FA00291 | Cable Tie , Natural 6", Inner Unit Pack: 100 pieces per box | Box | 1 | 11 | 11
32 | FA00292 | Cable Tie, Natural 8", Inner Unit Pack: 100 pieces per box | Box | 1 | 11 | 11
33 | FA00293 | Cable Tie, Natural 12", inner Unit Pack: 100 pieces per box | Box | 1 | 11 | 11
34 | FA00294 | Cable Tie, Heavy Duty Weather Resistant 8", Inner Unit Pack: 100 per box | Box | 1 | 11 | 11
35 | FA00295 | Cable Tie , Heavy Duty Weather Resistant 12", Inner Unit Pack: 100 pieces per box | Box | 1 | 11 | 11
F |  | Solar Power (12KW)
1 | FA00825 | VRLA Battery- 2V/760 AH @ C10 @ 1.75 ECV @ 27 Deg.C (+)48V DC, 760 AH * 2 nos = 1520 AH per site with battery racks, stands, connectors, battery remover, transparent covers,etc Make:HBL/Amaraja/Rocket/NED | Banks | 1 | 3 | 3
2 | FA00613 | Solar Modules/Panels with structures ie 1.5M above the ground level, Wattage (Wp): 335 Wp Voltage (Vmp) : 36 V Current (Imp) : 8 Amps with mounting structures (6 module structure), pre-assembled connectors ( 12KW capacity) ( Tata BP/ Vikram solar/ Mosebaer) 36 Module per site (Tata BP/ Vikram solar/ Mosebaer/Waree/Equivalent) | PV/module | 36 | 108 | 3888
3 | FA00839 | Solar Structure ie 1.5M above ground level foundation bolts and templates for 6 module structure with 36 panels. | Set | 1 | 3 | 3
4 | FA00642 | Surge Protection Device, Un (dc) = 48V, Uc (dc) = 75V, In (8/20μs)= 40kA with appropriate MCB and BOX prewired with fault indicator available, Make Erico/Eritech/Tercel/Dehn/LPI/Phoenix | No | 1 | 3 | 3
5 | FA00276 | ACPDB (Rating: 100 amps, 230 V AC Pre-wired/assembled with inbuilt MCBs (2P, 32 amps - 4 Nos, 2 P, 16 amps- 8 Nos, 2P, 10 amps- 6 nos ) | No | 1 | 3 | 3
6 | FA00275 | DCPDB ( Rating: 100amps, -48VDCPDC. This Pre-wired Power Distribution Board shall provide all the connections to battery bank with proper rating of DC MCBs and additional battery charging facilities. MCB dual pole rating as 63A 2 nos, 32A 4nos, 16A 10nos | No | 1 | 3 | 3
7 | FA00829 | Solar-DG-Utility-Battery Hybrid MPPT system, modular type, 2 kW, 500 Amps, having min 6 (Five) solar mppt modules of 40 Amps capacity and 2 additional MPPT slots . 6 nos of rectifier module of capacity 80 amps and 2 additional rectifier slots having the following features: Must have load facility to connect both critical and non critical loads using appropriate MCBs and HRC Fuse. Further, the system also should have min two nos of appropriate rating of HRC fuses for connecting of min two battery banks of min 450 Ah per bank. Also should have an inbuilt controller having the following features to monitor the status of the rectifier, battery, room temperature, ac mains available or not, DG supply available or not, rectifier failure alarm, load on battery, load on AC or DG. All these parameters are to be monitored remotely using LAN/Modem, GSM, GPRS, Web browser. Remote alarming using dry contacts/SNMP: 1. Solar Converter Specs: Input voltage (DC), Vertiv/Delta/Eltek/Dynamic Power/Exicom | set | 1 | 3 | 3
8 | FA00830 | Solar DC Power Cables: Specification: 1. Construction: tinned copper conductor IEC 60228, insulation/sheath: electron beam cross linked halogen free & flame retardant component. 2. Electrical: Max permissible operating voltage: DC 1.8kV 3. Temperature: -40 to +90 Deg C., Solar Panel to AJB: 6 sq.mm, (RED) 50 m per site (Polycab/ RR/Havell's/Relison ) | nos | 1 | 3 | 3
9 | FA00831 | Solar DC Power Cables: Specification: 1. Construction: tinned copper conductor IEC 60228, insulation/sheath: electron beam cross linked halogen free & flame retardant component. 2. Electrical: Max permissible operating voltage: DC 1.8kV 3. Temperature: -40 to +90 Deg C., ) Solar Panel to AJB: 6 sq.mm, (BLACK) 50 m per site (Polycab/ RR/Havell's /Relison | nos | 1 | 3 | 3
10 | FA00832 | Solar Cable Armoured Specification for 12KW Solar system: 1. Construction: tinned copper conductor IEC 60228, insulation/sheath: electron beam cross linked halogen free & flame retardant component. 2. Electrical: Max permissible operating voltage: DC 1.8kV 3. Temperature: -40 to +90 Deg C. 4. Armour: braid of galvanized steel, , AJB to Hybrid Rectifier: 16sq.mm, 2C, solar dc cable, multistand copper conductor 120M per site (Polycab/ RR/Havell's/Relison ) | No | 1 | 3 | 3
11 | FA00843 | DC Power Cable, Hybrid Charger to Battery Bank: 90 sq.mm, 1C, PVC insulated, multistrand copper conductor (RED ) 50 m per site (Polycab/ RR/Havell's /Relison) | No | 1 | 3 | 3
12 | FA00834 | DC Power Cable, Hybrid Charger to Battery Bank: 90 sq.mm, 1C, PVC insulated, multistrand copper conductor (BLACK ) 50 m per site (Polycab/ RR/Havell's /Relison) | No | 1 | 3 | 3
13 | FA00017 | Installation Materials | No | 1 | 3 | 3
14 | FA00284 | Chemical Based Earthing System with -48VDC DC SPD:CHEMICAL EARTHING . CPRI /ISO Approved Chemical earthing . Tri-rod pre welded copper (5 ft long 12mm Dia. # 2 set), GAF (Chemical) # 2X40 kg, Copper revit # 10 nos, Earth Distribution bus bar # 2 Nos, earth pit cover, copper strip 25X3 mm. # 30 mtr per set, salt # 2 X 10 kg per set, Charcoal # 2 x 5 kg per set, connectors, lugs,clamps, etc Surge Protection Device, Un (dc) = 48V, Uc (dc) = 75V, In (8/20μs)= 40kA with appropriate MCB and BOX prewired with fault indicator available (BSMC/Eritech/ Icon/Pragati) | No | 1 | 3 | 3
15 | FA00475 | Earth Cable ( Green or Green/yellow mixed), PVC insulated single multi strand core copper conductor ( 1.1KV) 1C , 25 sq.mm (50M per site) (Make: Polycab/ RR/Havell's) | No | 1 | 3 | 3
16 | FA00605 | Free Cooling Unit, Air outlet configuration Gravity based dampers without any fan. Worm-protection net. The assembly shall ensure no water / rain leak into the shelter. The damper is closed when AC is operating and damper will open when FCU is operating Air inlet configuration Rain-proof cover, 48 V DC powered Axial flow fan, air filtering net, Gravity based dampers, worm-protection net, fine filters Filtration 90% down to 20 microns Airflow at full capacity 1200 + 200 CFM at 48 V (May be suitably designed as per site requirement). 2/4 fans may be used to meet the total CFM requirement, if required. Microprocessor based controller The Control unit (controller) shall be provided to automatically control the operation of FCU in all possible conditions in telecommunications equipment room in auto mode. It shall also have facility to switch on and off the air conditioning units installed in the room. Auto Mode Operation – 1. Under favorable environment conditions, the controller shall switch off the air-conditioning unit and start free cooling. 2. Whenever room temperature rises above set temperature, then controller shall switch off the FCU / associated dampers and switch on the air-conditioning unit. 3. The controller shall switch off the FCU / associated dampers if battery voltage drop below set voltage. 4. Controller shall measure Run Hour of FCU Mode and Cooling Mode. 5. When ever the temperature of BTS exceeds 40 Deg C on a/c of AC failure or any other reason, there should be a provision to start Free Cooling Unit again through controller for emergency cooling ( Pragati/ICON/Delta/Vertiv) | Set | 1 | 3 | 3
17 | FA00622 | DC/AC lighting system in Shelter, 48V dc light or 230v AC tubelight with switch | Set | 1 | 3 | 3
18 | FA00649 | AC lighting system in Shelter, 230v AC tubelight with switch & accessories | Set | 1 | 3 | 3
19 | FA00287 | LPS ( Lightening Protection System) - 1. Lightning Arrester: Supply of Lightning Protection System that works on Early Streamer Emission Technology having coverage radius >80 mtrs when mounted at a height of 05 mtrs giving level I protection. Tested international high-tension laboratory, tested/approved by CPRI, India 2. FRP Mast-5 mtrs. 3.Lightning Strike Counter with IP-65 Enclosure 4. HVSC Down Copper conductor 5. Chemical Earthing: i. Tri-rod 100% copper (5 ft long 17mm Dia # 2 set) welded together and with connection strip & fitted with 4 sets for connecting ii. GEM (Chemical) # 2X40 kg iii. Copper rivet # 10 nos iv. Earth Distribution bus bar # 2 Nos, v. Earth pit cover - 2 nos. vi. Copper (100% copper) strip 25X3 mm- 30 mtr vii. Connectors, lugs, clamps, etc (Make: LPI/Erico/Bakiral) | No | 1 | 3 | 3
20 | FA00606 | Split Type Airconditioners ( Stabiliser free, inverter air conditioner: 1.5T, Single Phase,50Hz,Input Volt=150 - 230V, Split type with appropriate rating of MCBs,High Low Pressure Pipe=4 m each, outlet drain pipe =10 m each flexible, cable size=4 sqmm cu stranded 3 core=5 m, MCBs=SPN, 16Amps, with stand to fix the outdoor unit. Refrigerant: R32 (Make: Samsung/Hitachi/Toshiba/Blue star/ LG/Voltas/Godrej/Daikin) | Set | 1 | 3 | 3
21 | FA00645 | Solar Junction Box , Array Junction Box (min 4 inputs and 1 output), | Set | 6 | 18 | 108
22 | FA00625 | Copper Terminal Lugs, 6 sq.mm ( 20 nos Ring type) | Pkt | 1 | 3 | 3
23 | FA00626 | Copper Terminal Lugs, 6 sq.mm ( 10 nos pin type) | Pkt | 1 | 3 | 3
24 | FA00609 | Copper Terminal Lugs, 25 sq.mm ( 20 nos Ring type) | Pkt | 1 | 3 | 3
25 | FA00840 | Copper Terminal Lugs, 25 sq.mm ( 10 nos pin type) | Pkt | 1 | 3 | 3
26 | FA00611 | Copper Terminal Ends Lugs, 90 sq.mm ( 15 nos Ring type) | Pkt | 1 | 3 | 3
27 | FA00651 | Copper Terminal Lugs, 16 sq.mm (25 nos pin Type ) | Pkt | 1 | 3 | 3
28 | FA00488 | PVC Insulation Tape RED | Roll | 2 | 6 | 12
29 | FA00489 | PVC Insulation Tape ( Black) | Roll | 2 | 6 | 12
30 | FA00492 | PVC Insulation Tape ( Green) | Roll | 2 | 6 | 12
31 | FA00291 | Cable Tie , Natural 6", Inner Unit Pack: 100 pieces per box | Box | 1 | 3 | 3
32 | FA00292 | Cable Tie, Natural 8", Inner Unit Pack: 100 pieces per box | Box | 1 | 3 | 3
33 | FA00293 | Cable Tie, Natural 12", inner Unit Pack: 100 pieces per box | Box | 1 | 3 | 3
34 | FA00294 | Cable Tie, Heavy Duty Weather Resistant 8", Inner Unit Pack: 100 per box | Box | 1 | 3 | 3
35 | FA00295 | Cable Tie , Heavy Duty Weather Resistant 12", Inner Unit Pack: 100 pieces per box | Box | 1 | 3 | 3
F |  | DG set
1 | FA00835 | DG 20 KVA , Single Phase (230V, 50Hz), 1500rpm and 0.8 PF, sound and weather proof canopy outdoor unit including cold starting kit, AMF Panel with inbuilt DC-DC Converter (48V input & 12V output), Fuel Tank (300Litres), 25Sqmm single phase armoured PVC insulated copper cable with 15 meters per site, Earth Cables 15 mtrs each site with other accessories including lugs with Central Monitoring System (CMS) ( Jackson (Cummins)/ TMTL Eicher) | Set | 1 | 22 | 22
2 | FA00284 | Chemical Based Earthing System with -48VDC DC SPD:CHEMICAL EARTHING . CPRI /ISO Approved Chemical earthing . Tri-rod pre welded copper coated (5 ft long 12mm Dia. # 2 set), GAF (Chemical) # 2X40 kg, Copper revit # 10 nos, Earth Distribution bus bar # 2 Nos, earth pit cover, copper strip 25X3 mm. # 30 mtr per set, salt # 2 X 10 kg per set, Charcoal # 2 x 5 kg per set, connectors, lugs,clamps, etc Surge Protection Device, Un (dc) = 48V, Uc (dc) = 75V, In (8/20μs)= 40kA with appropriate MCB and BOX prewired with fault indicator available (BSMC/Eritech/ Icon/Pragati) | Set | 1 | 22 | 22
G |  | Other Materials
1 | FA00175 | 19" Rack 27U ( 1.75M height with full mounting accessories) | No | 1 | 88 | 88
2 | FA00301 | Antenna Mounting Structure (Tower leg/angle) | No | 1 | 359 | 359
3 | FA00836 | Antenna Mounting Structure (Monopole) | No | 1 | 117 | 117
4 | FA00400 | Roxtec | No | 1 | 71 | 71
H |  | Additional Power Equipment
1 | FA00275 | DCPDB ( Rating: 100amps, -48VDCPDC. This Pre-wired Power Distribution Board shall provide all the connections to battery bank with proper rating of DC MCBs and additional battery charging facilities. MCB dual pole rating as 63A 2 nos, 32A 4nos, 16A 10nos | No | 1 | 124 | 124
2 | FA00276 | ACPDB (Rating: 100 amps, 230 V AC Pre-wired/assembled with inbuilt MCBs (2P, 32 amps - 4 Nos, 2 P, 16 amps- 8 Nos, 2P, 10 amps- 6 nos ) | No | 1 | 11 | 11
3 | FA00837 | VRLA Battery- 2V/1000 AH @ C10 @ 1.75 ECV @ 27 Deg.C (+)48V DC, 1000 AH * 2 nos = 2000 AH per site with battery racks, stands, connectors, battery remover, transparent covers,etc Make:HBL/Amaraja/Rocket/NED | Banks | 1 | 1 | 1
4 | FA00838 | VRLA Battery- 2V/760 AH @ C10 @ 1.75 ECV @ 27 Deg.C (+)48V DC, 760 AH * 2 nos = 1520 AH per site with battery racks, stands, connectors, battery remover, transparent covers,etc Make:HBL/Amaraja/Rocket/NED | Banks | 1 | 2 | 2
5 | FA00602 | SMPS Rectifier Battery Charger, IP Vac = 180 – 280 Vac; OP = (-48V DC), 500 Amps, Modular Type with minimum 8 No of Modules and 8 slots of 60 Amps per module. Must have load facility to connect both critical and non critical loads using appropriate MCBs and HRC Fuse. Also should have an inbuilt controller having the following features to monitor the status of the rectifier, battery, room temperature, ac mains available or not, DG supply available or not, rectifier failure alarm, load on battery, load on AC or DG. All these parameters are to be monitored remotely using LAN/Modem, GSM, GPRS, Web browser. Remote alarming using dry contacts/SNMP. ( Vertiv/Delta / benning/Dynamic Power) | No | 1 | 1 | 1
6 | FA00287 | LPS ( Lightening Protection System) - 1. Lightning Arrester: Supply of Lightning Protection System that works on Early Streamer Emission Technology having coverage radius >80 mtrs when mounted at a height of 05 mtrs giving level I protection. Tested international high-tension laboratory, tested/approved by CPRI, India 2. FRP Mast-5 mtrs. 3.Lightning Strike Counter with IP-65 Enclosure 4. HVSC Down Copper conductor 5. Chemical Earthing: i. Tri-rod 100% copper (5 ft long 17mm Dia # 2 set) welded together and with connection strip & fitted with 4 sets for connecting ii. GEM (Chemical) # 2X40 kg iii. Copper rivet # 10 nos iv. Earth Distribution bus bar # 2 Nos, v. Earth pit cover - 2 nos. vi. Copper (100% copper) strip 25X3 mm- 30 mtr vii. Connectors, lugs, clamps, etc (Make: LPI/Erico/Bakiral) | Set | 1 | 10 | 10
7 | FA00841 | AC Power Cable, 1.1kV,2C PVC insulated, unarmored multi-strand aluminum cable 35sqmm (Polycab/ RR/Havell's/Relison ) | m | 1 | 9640 | 9640
8 | FA00842 | AC Power Cable,1.1KV, 2C-Single Phase, UG armored, aluminum cable 35sqmm (Polycab/ RR/Havell's/Relison ) | m | 1 | 8400 | 8400
I |  | Services
1 | SW00588 | Transporation of Tower and foundation materials to designated site | nos | 1 | 70 | 70
2 | SW00589 | Dismantling and Transportation of Tower and foundation materials from Kabesa, Punakha to Dechencholing check post | nos | 1 | 1 | 1
3 | SW00590 | 35M 3Legged Tower Erection including earthing | nos | 1 | 2 | 2
4 | SW00591 | 30M 3Legged Tower Erection including earthing | nos | 1 | 34 | 34
5 | SW00592 | 25M 3Legged Tower Erection including earthing | nos | 1 | 28 | 28
6 | SW00593 | 20M 3Legged Tower Erection including earthing | nos | 1 | 6 | 6
7 | SW00594 | 15M 4Legged Tower erection at Dechencholing check post including earthing | nos | 1 | 1 | 1
8 | SW00595 | Transporation of shelter and foundation materials to designated site | nos | 1 | 71 | 71
9 | SW00596 | Shelter Erection including earthing | nos | 1 | 70 | 70
10 | SW00597 | Shelter Erection :6000x3600x2600 including earthing | nos | 1 | 1 | 1
11 | SW00598 | Transporation of AC Power to designated site | nos | 1 | 50 | 50
12 | SW00599 | Transporation of Solar Power and foundation to designated site | nos | 1 | 14 | 14
13 | SW00600 | Installation of AC Power including earthing, etc as per details provided | nos | 1 | 50 | 50
14 | SW00601 | Installation of 10KW Solar Power including earthing, etc as per details provided | nos | 1 | 11 | 11
15 | SW00602 | Installation of 12KW Solar Power including earthing, etc as per details provided | nos | 1 | 3 | 3
16 | SW00603 | Transportation of DEG to designated sites | nos | 1 | 22 | 22
17 | SW00604 | Installation of DEG including earthings | nos | 1 | 22 | 22
18 | SW00605 | Transporation of Monopole and foundation materials to designated site | nos | 1 | 50 | 50
19 | SW00606 | Monopole Erection including earthing and lighting | nos | 1 | 50 | 50

## TPSD Service BOQ
Annnexure-I BOM for Transportations of tower, power, shelter and DEGs
[19 empty] | Local Transportation from Phuntsholing to Site(Option-1) |  |  |  |  | Erection & Installation |  |  |  |  | Total Cost | Remarks
SN |  | Regions | PC | Site Name | Power system | Walking distance from nereast road without load | Distance from main road KM(Approx) | AC Power |  | Solar Power |  |  |  | DG Weight with tanks+earthing set(Kg) | Shelter with cable tray (Kg) | Tower (Kg) | Total Weight(Kg) | Tower Type | Tower | AC Power | Solar Power | DG | Shelter | Tower including earthing | AC Power including earthing | Solar Power including earthing | DG including earthing | Shelter including earthing
| Item Code | [6 empty] | Power items ( rectifiers/AC/ventilations/AC-DC PDB/LPI/Rack/Roxtec/earthing including cables & accessories (Kg) | Battery with enclosure Weight (Kg) | Solar panels (Kg) | Solar 6 module mounting structures weight with AJBs(Kg) | Power items ( rectifiers/AC/ventilations/AC-DC PDB/LPI/19"rack/Roxtec/earthing including cables & accessories (Kg) | Battery with enclosure Weight (Kg)
1 |  | ER | Lhuentse | Dekeling/Katphu_Tsenkhar Gewog | BPC+ Solar | 3 hrs | 60 km | NA | NA | 660 | 560 | 1100 | 1500 | NA | 1300 | 3800 | 8920 | 25mx3L | Yes | No | Yes | No | Yes | Yes | No | Yes | No | Yes
2 |  | ER | Lhuentse | Zamling/Khauchung Chewog under Gangzur gewog | AC power + DEG | 20 mins | 30 km | 1100 | 1500 | NA | NA | NA | NA | 1100 | 1300 | 3800 | 8800 | 25mx3L | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes
3 |  | ER | Lhuentse | Ongar Chiwog under Metsho Gewog (Hydro power) | AC power + DEG | 1.5 hr from the nearest road point | 65 km | 1100 | 1500 | NA | NA | NA | NA | 1100 | 1300 | 3800 | 8800 | 25mx3L | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes
4 |  | ER | Lhuentse | Rafla | N/A | 6 hrs from the nearsest road point | 27 km | NA | NA | NA | NA | NA | NA | NA | NA | 3000 | 3000 | 20mx3L | Yes | No | No | No | No | Yes | No | No | No | No
5 |  | ER | Mongar | Resa village | AC power | 1.5 hr | 27 km | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 3800 | 7700 | 25mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
6 |  | ER | Mongar | Bompazor Chiwog_Drepong Gewog | AC power | 1.5 hr | 27 km | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 3800 | 7700 | 25mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
7 |  | ER | Mongar | Lingmethang | AC Power | N.A |  | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | NA | 3900 | NA | No | Yes | No | No | Yes | No | Yes | No | No | Yes
8 |  | ER | Pemagatshel | Gamung-Shali chiwog under Shumar Gewog | AC power | 1.5 hr | 12 kM | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 3800 | 7700 | 25mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
9 |  | ER | Pemagatshel | Loongkholom Chiwog under Chimmong Gewog | AC power | 1hr | 55 km | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 3800 | 7700 | 25mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
10 |  | ER | Pemagatshel | Duringri village under Mekuri Chowig | AC Power | 1 hr | 98 km | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 3800 | 7700 | 25mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
11 |  | ER | Samdrupjongkhar | Martang | Ac power | 1 hr | 40 km | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 3800 | 7700 | 25mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
12 |  | ER | Samdrupjongkhar | Metogang | Ac power + DEG | 30 mins | 4 km | 1100 | 1500 | NA | NA | NA | NA | 1100 | 1300 | 3800 | 8800 | 25mx3L | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes
13 |  | ER | Samdrupjongkhar | Sachilo_Wangphoog gewog | AC power | 1 hr | 140 km | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 5050 | 8950 | 30mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
14 |  | ER | Samdrupjongkhar | Merinchengma | N/A | 3 hrs | 70 km | NA | NA | NA | NA | NA | NA | NA | 1300 | NA | 1300 | NA | No | No | No | No | Yes | No | No | No | No | Yes
15 |  | ER | Trashigang | Khelephu | Solar+BPC | 1 day walk from Tsothang | 80 km | NA | NA | 660 | 560 | 1100 | 1500 | NA | 1300 | 3800 | 8920 | 25mx3L | Yes | No | Yes | No | Yes | Yes | No | Yes | No | Yes
16 |  | ER | Trashigang | Khasheteng | Solar+BPC | 4 hrs from the nearest roadpoint | 65km | NA | NA | 660 | 560 | 1100 | 1500 | NA | 1300 | 3800 | 8920 | 25mx3L | Yes | No | Yes | No | Yes | Yes | No | Yes | No | Yes
17 |  | ER | Trashigang | Bikhar | AC power +DEG | 30 mins | 40 km | 1100 | 1500 | NA | NA | NA | NA | 1100 | 1300 | 5050 | 10050 | 30mx3L | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes
18 |  | ER | Trashigang | Phomshing | AC power | 30 mins | 1km | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 5050 | 8950 | 30mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
19 |  | ER | Trashigang | Yonphula new site | Ac power + DEG | 25 mins | 30 km | 1100 | 1500 | NA | NA | NA | NA | 1100 | 1300 | 5050 | 10050 | 30mx3L | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes
20 |  | ER | Trashiyangtse | Dechen Phodrang | Ac power + DEG | 1 hr | 47 km | 1100 | 1500 | NA | NA | NA | NA | 1100 | 1300 | 5050 | 10050 | 30mx3L | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes
21 |  | ER | Trashiyangtse | Boomdeling_Regilam | N/A | 1.5 hr | 10 km | NA | NA | NA | NA | NA | NA | NA | NA | 5050 | 5050 | 30mx3L | Yes | No | No | No | No | Yes | No | No | No | No
22 |  | ER | Trashiyangtse | Ramjar RS | N/A | N.A | 50 km | NA | NA | NA | NA | NA | NA | NA | NA | 3800 | 3800 | 25mx3L | Yes | No | No | No | No | Yes | No | No | No | No
23 |  | ER | Samdrupjongkhar | Nganglam Exchange (Colocation Shelter) | N/A |  |  | NA | NA | NA | NA | NA | NA | NA | 2200 | NA | 2200 | NA | No | No | No | No | Yes | No | No | No | No | Yes
24 |  | CR | Bumthang | Jilikhar extended LAP | AC Power+DEG | 10mins | 3KM | 1100 | 1500 | NA | NA | NA | NA | 1100 | 1300 | 3800 | 8800 | 25mx3L | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes
25 |  | CR | Bumthang | Lamigonpa | Solar Power+BPC | 15mins | 7KM | NA | NA | 660 | 560 | 1100 | 1500 | NA | 1300 | 3800 | 8920 | 25mx3L | Yes | No | Yes | No | Yes | Yes | No | Yes | No | Yes
26 |  | CR | Bumthang | Zangtherpo | AC Power+DEG | 40 Minutes | 6km | 1100 | 1500 | NA | NA | NA | NA | 1100 | 1300 | 3800 | 8800 | 25mx3L | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes
27 |  | CR | Zhemgang | Goling | Solar Power+DEG+BPC | 30mins | 16km | NA | NA | 660 | 560 | 1100 | 1500 | 1100 | 1300 | 5050 | 11270 | 30mx3L | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes
28 |  | CR | Zhemgang | Dali | Solar Power+DEG+BPC | 30mins | 41km | NA | NA | 660 | 560 | 1100 | 1500 | 1100 | 1300 | 3800 | 10020 | 25mx3L | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes
29 |  | CR | Zhemgang | Buli | Solar Power+DEG+BPC | 30mins | 50Km | NA | NA | 660 | 560 | 1100 | 1500 | 1100 | 1300 | 3800 | 10020 | 25mx3L | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes
30 |  | CR | Zhemgang | Pantang | Solar Power+DEG+BPC | 25mins | 25Km | NA | NA | 660 | 560 | 1100 | 1500 | 1100 | 1300 | 5050 | 11270 | 30mx3L | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes
31 |  | CR | Damphu | Lungsigang | AC Power+DEG | 20 mins | 18km | 1100 | 1500 | NA | NA | NA | NA | 1100 | 1300 | 5050 | 10050 | 30mx3L | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes
32 |  | CR | Damphu | Drujaygang | DEG | 5 mins | 54km | NA | NA | NA | NA | NA | NA | 1100 | NA | 5050 | 6150 | 30mx3L | Yes | No | No | Yes | No | Yes | No | No | Yes | No
33 |  | CR | Damphu | Phuntenchu | Solar Power+DEG+BPC | 5 mins | 62km | NA | NA | 660 | 560 | 1100 | 1500 | 1100 | 1300 | 3800 | 10020 | 25mx3L | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes
34 |  | CR | Trongsa | Semji Vilklage | AC Power+DEG | 1 hrs | 10km | 1100 | 1500 | NA | NA | NA | NA | 1100 | 1300 | 3000 | 8000 | 20mx3L | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes
35 |  | CR | Dagapela | Khebisa | N/A | 3mins | 30km | NA | NA | NA | NA | NA | NA | NA | NA | 3800 | 3800 | 25mx3L | Yes | No | No | No | No | Yes | No | No | No | No
36 |  | CR | Dagapela | Tanabji | N/A | 30mins | 32km | NA | NA | NA | NA | NA | NA | NA | NA | 3800 | 3800 | 25mx3L | Yes | No | No | No | No | Yes | No | No | No | No
37 |  | CR | Bumthang | Thangbi | N/A | 3mins | 15km | NA | NA | NA | NA | NA | NA | NA | NA | 3800 | 3800 | 25mx3L | Yes | No | No | No | No | Yes | No | No | No | No
38 |  | CR | Zhemgang | Galabi | AC power Except Battery and LPI | 5mins | 3Km | 1100 | NA | NA | NA | NA | NA | NA | 1300 | NA | 2400 | NA | No | Yes | No | No | Yes | No | Yes | No | No | Yes
39 |  | CR | Gelephu | Alleydara | AC Power with 760AH | 5mins | 37Km | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | NA | 3900 | NA | No | Yes | No | No | Yes | No | Yes | No | No | Yes
40 |  | CR | Zhemgang | Phawa top | AC power Except Battery and LPI | 20mins | 55Km | 1100 | NA | NA | NA | NA | NA | NA | 1300 | NA | 2400 | NA | No | Yes | No | No | Yes | No | Yes | No | No | Yes
41 |  | CR | Zhemgang | Manas | BPC+Solar+DEG | 15mins | 13Km | NA | NA | 660 | 560 | 1100 | 1500 | 1100 | 1300 | 5050 | 11270 | 30mx3L | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes
42 |  | CR | Zhemgang | Serkem Lhaptsa (RS for Manas Site+BTS) | BPC+Solar+DEG |  |  | NA | NA | 660 | 560 | 1100 | 1500 | 1100 | 1300 | 5050 | 11270 | 30mx3L | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes
43 |  | CR | Zhemgang | Sorapang (Tcell tower sharing) | Solar Power |  |  | NA | NA | 660 | 560 | 1100 | 1500 | NA | 1300 | NA | 5120 | NA | No | Yes | No | No | Yes | No | Yes | No | No | Yes
44 |  | SWR | Samtse | Uttaray | AC Power | 30 minutes | 50KM | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 3800 | 7700 | 25mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
45 |  | SWR | Samtse | Nimalung | AC Power+BPC | 45 minutes | 30KM | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 5050 | 8950 | 30mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
46 |  | SWR | Samtse | Chugo | AC Power | 25 minutes | 112KM | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 3800 | 7700 | 25mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
47 |  | SWR | Samtse | Sathgharay | AC Power+BPC | 30 minutes | 55KM | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 5050 | 8950 | 30mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
48 |  | SWR | Samtse | Samatar | AC Power | 10 minutes | 60KM | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 5050 | 8950 | 30mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
49 |  | SWR | Samtse | Sibichang (Thulunggang Top) | AC Power+BPC | 30 minutes | 50KM | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 3800 | 7700 | 25mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
50 |  | SWR | Phuentsholing | Lhamoizingkha Sibsooney top | AC Power+BPC | 10 minutes | 5KM | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 5050 | 8950 | 30mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
51 |  | SWR | Phuntsholing | Chilaunay | AC Power | 20 minutes | 12KM | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 3800 | 7700 | 25mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
52 |  | SWR | Gedu | Darla-Dhamdara | AC Power | 20 minutes | 10KM | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 3800 | 7700 | 25mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
53 |  | SWR | Gedu | Susigang (Chitraydara/Getena) | AC Power |  | 40KM | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 5050 | 8950 | 30mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
54 |  | SWR | Gedu | Near Lhamoizingkha tsho HW | Solar Power (12KW) | 50 minutes | 65KM | NA | NA | 760 | 660 | 1100 | 2000 | NA | 1300 | 3800 | 9620 | 25mx3L | Yes | No | Yes | No | Yes | Yes | No | Yes | No | Yes
55 |  | SWR | Gedu | Gedu Town | N/A | 5mins | 1KM | NA | NA | NA | NA | NA | NA | NA | 1300 | NA | 1300 | NA | No | No | No | No | Yes | No | No | No | No | Yes
56 |  | SWR | Gedu | Tala top | N/A | 25mins | 3KM | NA | NA | NA | NA | NA | NA | NA | 1300 | NA | 1300 | NA | No | No | No | No | Yes | No | No | No | No | Yes
57 |  | SWR | Gedu | Chapcha | N/A | 10mins | 65KM | NA | NA | NA | NA | NA | NA | NA | NA | 5050 | 5050 | 30mx3L | Yes | No | No | No | Yes | Yes | No | No | No | Yes
58 |  | SWR | Samtse | Tachey top | N/A | 20mins | 68KM | NA | NA | NA | NA | NA | NA | NA | NA | 3800 | 3800 | 25mx3L | Yes | No | No | No | Yes | Yes | No | No | No | Yes
59 |  | SWR | Samtse | Relukha | N/A | 25mins | 80KM | NA | NA | NA | NA | NA | NA | NA | 1300 | NA | 1300 | 20mx3L | Yes | No | No | No | Yes | Yes | No | No | No | Yes
60 |  | SWR | Samtse | Pugli | N/A | 0mins | 45KM | NA | NA | NA | NA | NA | NA | NA | 1300 | NA | 1300 | NA | No | No | No | No | Yes | No | No | No | No | Yes
61 |  | SWR | Samtse | Tendu | N/A | 5mins | 77KM | NA | NA | NA | NA | NA | NA | NA | 1300 | NA | 1300 | NA | No | No | No | No | Yes | No | No | No | No | Yes
62 |  | WR | Paro | Soe Gaygo Chumo | Solar Power | 3days walk without headload |  | NA | NA | 660 | 560 | 1100 | 1500 | NA | 1300 | 3050 | 8170 | 20mx3L | Yes | No | Yes | No | Yes | Yes | No | Yes | No | Yes
63 |  | WR | Thimphu | Tshaphu | AC Power | 20 Minutes |  | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 3000 | 6900 | 20mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
64 |  | WR | Paro | Chugjeykha Dratshang | AC Power | 10 Minutes |  | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 5050 | 8950 | 30mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
65 |  | WR | Wangdue | Ada | AC Power | 30 Minutes | 49KM | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 5050 | 8950 | 30mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
66 |  | WR | Wangdue | Uma | AC Power | 10 Minutes | 36KM | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 5050 | 8950 | 30mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
67 |  | WR | Wangdue | Sha gogana | AC Power | 10 Minutes | 90KM | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 5050 | 8950 | 30mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
68 |  | WR | Wangdue | Tshengeypokpo | AC Power | 20 Minutes | 85KM | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 5050 | 8950 | 30mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
69 |  | WR | Wangdue | Dangchu (Gobja) | AC Power | 30 Minutes | 65KM | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 5050 | 8950 | 30mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
71 |  | WR | Haa | Sangbaykha (Nakha-Tashigang) | Ac power + DEG | 10 Minutes |  | 1100 | 1500 | NA | NA | NA | NA | 1100 | 1300 | 6300 | 11300 | 35mx3L | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes
72 |  | WR | Haa | Samar gewog (Koina) | Ac power + DEG | 10 Minutes |  | 1100 | 1500 | NA | NA | NA | NA | 1100 | 1300 | 5050 | 10050 | 30mx3L | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes
73 |  | WR | Haa | Naja, Rashigang | AC Power | 20 Minutes |  | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 5050 | 8950 | 30mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
74 |  | WR | Gasa | Gasa new Town | Ac power + DEG | Road point |  | 1100 | 1500 | NA | NA | NA | NA | 1100 | 1300 | 5050 | 10050 | 30mx3L | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes
75 |  | WR | Punakha | Rangrikha | AC Power | 10 Minutes |  | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 5050 | 8950 | 30mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
76 |  | WR | Punakha | Khyimchena (Sewla) | AC Power | 20 Minutes |  | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 5050 | 8950 | 30mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
77 |  | WR | Punakha | Pangserpoo | AC Power | 20 Minutes |  | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 5050 | 8950 | 30mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
78 |  | WR | Haa | Suchhu (18MW Hydropower) | Ac power + DEG | Road point |  | 1100 | 1500 | NA | NA | NA | NA | 1100 | 1300 | 5050 | 10050 | 30mx3L | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes
79 |  | WR | Paro | Paro-Thimphu Highway/Dogar | AC Power | 20 Minutes |  | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 3800 | 7700 | 25mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
80 |  | WR | Thimphu | Simtokha-Docula Highway | AC Power | 20 Minutes |  | 1100 | 1500 | NA | NA | NA | NA | NA | 1300 | 3050 | 6950 | 20mx3L | Yes | Yes | No | No | Yes | Yes | Yes | No | No | Yes
81 |  | WR | Punakha | Kabesa (Tower Replacement) | N/A |  |  | NA | NA | NA | NA | NA | NA | NA | NA | 5050 | 5050 | 30mx3L | Yes | No | No | No | No | Yes | No | No | No | No
82 |  | WR | Thimphu | Dechencholing Forest Checkpost (To be replaced with tower from Kabesa, Punakha) | N/A |  |  | NA | NA | NA | NA | NA | NA | NA | NA | 2200 | 2200 | 15mx3L | Yes | No | No | No | No | Yes | No | No | No | No
Note:
|  |  | 1 | Tower erection is including earthing
|  |  | 2 | Shelter installation is including earthing
|  |  | 3 | DEG installation is including earthing
|  |  | 4 | If the site have only tower then tower erection team needs to do erection, earthing and LPI installation.
|  |  | 5 | Please provide the breakup cost here.

## Monopole Service BOQ
SN | Regions | PC | Site Name | Headload | Tower | Tower Weight Kg (includes monopole & accessories) | Local Transportation from Phuntsholing to Site(Option-1) | Monopole Erection including earthing | Total
1 | ER | Pemagatshel | Denchi Town | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
2 | ER | Mongar | Lingmethang CDCL | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
3 | ER | Lhuentse | Khoma Village | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
4 | ER | Trashigang | Barshong_Dratshang | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
5 | ER | Samdrupjongkhar | Pinchina | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
6 | ER | Samdrupjongkhar | DCCL_Nganglam | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
7 | ER | Trashigang | Khaling Town | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
8 | CR | Bumthang | Pongkhar/Jakar village | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
9 | CR | Zhemgang | Panbang RBP area | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
10 | CR | Zhemgang | Tingtibi | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
11 | CR | Zhemgang | Zhemgang town | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
12 | CR | Sarpang | Schemthang town (Helley) | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
13 | CR | Trongsa | NHDCL colony | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
14 | CR | Trongsa | Dzongkhalung | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
15 | CR | Gelephu | Gelephu Site 1 | Roadpoint | 15m monopole-2 LED Slip joint | 1300 | Yes | Yes | Yes
16 | CR | Gelephu | Gelephu Site 2 | Roadpoint | 15m monopole-2 LED Slip joint | 1300 | Yes | Yes | Yes
17 | SWR | Gedu | Tsimasham old Dzong | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
18 | SWR | Gedu | Wangkha Colony | Roadpoint | 15m monopole-2 LED Slip joint | 1300 | Yes | Yes | Yes
19 | SWR | Phuentsholing | Namgay Grand | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
20 | SWR | Phuentsholing | Ahem Hotel Area | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
21 | WR | Thimphu | Phajoding (with manual Monopole with 5 Segment and outdorr IP radio) | 5 Hours | 15m monopole-3 LED Flange joint | 1300 | Yes | Yes | Yes
22 | WR | Thimphu | Simo | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
23 | WR | Thimphu | Dolung Goenpa (with manual Monopole with 5 Segment and outdoor IP radio) | 8 Hours | 15m monopole-3 LED Flange joint | 1300 | Yes | Yes | Yes
24 | WR | Haa | Katsho | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
25 | WR | Wangdue | RBA Tencholing | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
26 | WR | Paro | Gaupel Area | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
27 | WR | Punakha | Chubu Tshachu (with manual Monopole with 5 Segment and outdoor IP radio) | 10 Mins | 15m monopole-3 LED Flange joint | 1300 | Yes | Yes | Yes
28 | WR | Punakha | Nubgang | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
29 | WR | Punakha | Goenmsa | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
30 | WR | Thimphu | Kabesa | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes | Monopole to be relocated from Muscle Factory (2021 site)
31 | WR | Thimphu | Bebena-1 | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes | Monopole to be relocated from Changzamtok (2021 site)
32 | WR | Thimphu | Changangkha-1 | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes | Monopole to be relocated from Near Peaceful Resort (2021 site)
33 | WR | Thimphu | Babesa HS | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes | Monopole to be relocated from RICBL (2022 site)
34 | WR | Thimphu | Core Taba-1 | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes | Monopole to be relocated from Near Hotel Dusit (2022 site)
35 | WR | Thimphu | Core Taba-2 | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes | Monopole to be relocated from VVIP monopole (2021 site)
36 | WR | Thimphu | Near National HE | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
37 | WR | Thimphu | MPLS Lungtenzam | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
38 | WR | Thimphu | Changangkha-2 | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
39 | WR | Thimphu | Changjiji Colony | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
40 | WR | Thimphu | Kalabazer/Changidaphu | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
41 | WR | Thimphu | Lungtenphu highway | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
42 | WR | Thimphu | Babesa Expressway | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
43 | WR | Thimphu | Near thori Resort, Lungtenphu | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
44 | WR | Thimphu | Depsi | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
45 | WR | Thimphu | Above Babesa Top/ Semtokha Top | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
46 | WR | Thimphu | Welcome Gate | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
47 | WR | Thimphu | Pamtsho | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
48 | WR | Thimphu | Chamina | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
49 | WR | Wangdue | Jigmethangka Dsite | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
50 | WR | Haa | Damthang | Roadpoint | 15m monopole-3 LED Slip joint | 1300 | Yes | Yes | Yes
Note:
Please provide the breakup cost here.